## 11MOXA
Server Name | NP5650-16_6261
10.10.1.11
Model Name | NPort 5650-16
MAC Address | 00:90:E8:65:92:4C
Serial No. | 6261
Firmware Version | 3.7 Build 16082411
Serial Settings
| Alias |  | Baud rate | Data bits | Stop bits | Parity | FIFO | Flow ctrl | Interface
Port 1 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 2 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 3 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 4 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 5 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 6 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 7 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 8 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 9 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 10 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 11 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 12 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 13 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 14 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 15 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 16 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Operating Settings
Port | Operating mode | Packing length | Delimiter 1 | Delimiter 2 | Delimiter process | Force transmit
1 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
2 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
3 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
4 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
5 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
6 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
7 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
8 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
9 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
10 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
11 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
12 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
13 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
14 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
15 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
16 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1

## 12MOXA
Server Name | NP5650-16_6466
10.10.1.12
Model Name | NPort 5650-16
MAC Address | 00:90:E8:65:93:19
Serial No. | 6466
Firmware Version | 3.7 Build 16082411
Serial Settings
| Alias |  | Baud rate | Data bits | Stop bits | Parity | FIFO | Flow ctrl | Interface
Port 1 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 2 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 3 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 4 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 5 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 6 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 7 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 8 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 9 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 10 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 11 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 12 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 13 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 14 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 15 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 16 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Operating Settings
Port | Operating mode | Packing length | Delimiter 1 | Delimiter 2 | Delimiter process | Force transmit
1 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
2 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
3 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
4 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
5 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
6 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
7 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
8 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
9 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
10 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
11 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
12 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
13 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
14 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
15 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
16 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1

## 13MOXA
Server Name | NP5650-16_2109
10.10.1.13
Model Name | NPort 5650-16
MAC Address | 00:90:E8:42:32:20
Serial No. | 2109
Firmware Version | 3.5 Build 11080114
Serial Settings
| Alias |  | Baud rate | Data bits | Stop bits | Parity | FIFO | Flow ctrl | Interface
Port 1 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 2 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 3 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 4 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 5 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 6 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 7 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 8 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 9 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 10 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 11 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 12 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 13 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 14 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 15 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 16 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Operating Settings
Port | Operating mode | Packing length | Delimiter 1 | Delimiter 2 | Delimiter process | Force transmit
1 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
2 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
3 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
4 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
5 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
6 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
7 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
8 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
9 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
10 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
11 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
12 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
13 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
14 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
15 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
16 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1

## 14MOXA
Server Name | NP5650-16_5093
10.10.1.14
Model Name | NPort 5650-16
MAC Address | 00:90:E8:33:25:4D
Serial No. | 5093
Firmware Version | 3.3 Build 08042219
Serial Settings
| Alias |  | Baud rate | Data bits | Stop bits | Parity | FIFO | Flow ctrl | Interface
Port 1 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 2 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 3 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 4 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 5 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 6 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 7 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 8 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 9 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 10 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 11 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 12 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 13 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 14 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 15 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 16 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Operating Settings
Port | Operating mode | Packing length | Delimiter 1 | Delimiter 2 | Delimiter process | Force transmit
1 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
2 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
3 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
4 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
5 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
6 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
7 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
8 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
9 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
10 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
11 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
12 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
13 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
14 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
15 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
16 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1

## 15MOXA
Server Name | NP5650-16_5990
10.10.1.15
Model Name | NPort 5650-16
MAC Address | 00:90:E8:20:7A:48
Serial No. | 5990
Firmware Version | 3.3 Build 08042219
Serial Settings
| Alias |  | Baud rate | Data bits | Stop bits | Parity | FIFO | Flow ctrl | Interface
Port 1 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 2 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 3 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 4 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 5 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 6 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 7 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 8 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 9 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 10 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 11 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 12 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 13 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 14 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 15 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 16 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Operating Settings
Port | Operating mode | Packing length | Delimiter 1 | Delimiter 2 | Delimiter process | Force transmit
1 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
2 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
3 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
4 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
5 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
6 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
7 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
8 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
9 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
10 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
11 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
12 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
13 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
14 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
15 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
16 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1

## 16MOXA
Server Name | NP5650-16_6132
10.10.1.16
Model Name | NPort 5650-16
MAC Address | 00:90:E8:20:7A:D6
Serial No. | 6132
Firmware Version | 3.3 Build 08042219
Serial Settings
| Alias |  | Baud rate | Data bits | Stop bits | Parity | FIFO | Flow ctrl | Interface
Port 1 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 2 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 3 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 4 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 5 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 6 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 7 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 8 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 9 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 10 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 11 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 12 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 13 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 14 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 15 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 16 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Operating Settings
Port | Operating mode | Packing length | Delimiter 1 | Delimiter 2 | Delimiter process | Force transmit
1 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
2 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
3 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
4 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
5 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
6 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
7 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
8 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
9 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
10 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
11 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
12 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
13 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
14 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
15 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
16 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1

## 17MOXA (2)
Server Name | NP5650-16_5988
10.10.1.17
Model Name | NPort 5650-16
MAC Address | 00:90:E8:20:7A:46
Serial No. | 5988
Firmware Version | 3.3 Build 08042219
Serial Settings
| Alias |  | Baud rate | Data bits | Stop bits | Parity | FIFO | Flow ctrl | Interface
Port 1 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 2 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 3 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 4 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 5 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 6 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 7 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 8 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 9 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 10 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 11 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 12 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 13 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 14 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 15 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 16 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Operating Settings
Port | Operating mode | Packing length | Delimiter 1 | Delimiter 2 | Delimiter process | Force transmit
1 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
2 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
3 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
4 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
5 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
6 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
7 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
8 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
9 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
10 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
11 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
12 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
13 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
14 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
15 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
16 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1

## 18MOXA
Server Name | NP5650-16_5987
10.10.1.18
Model Name | NPort 5650-16
MAC Address | 00:90:E8:20:7A:45
Serial No. | 5987
Firmware Version | 3.3 Build 08042219
Serial Settings
| Alias |  | Baud rate | Data bits | Stop bits | Parity | FIFO | Flow ctrl | Interface
Port 1 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 2 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 3 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 4 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 5 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 6 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 7 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 8 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 9 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 10 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 11 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 12 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 13 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 14 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 15 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 16 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Operating Settings
Port | Operating mode | Packing length | Delimiter 1 | Delimiter 2 | Delimiter process | Force transmit
1 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
2 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
3 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
4 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
5 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
6 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
7 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
8 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
9 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
10 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
11 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
12 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
13 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
14 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
15 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
16 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1

## 19MOXA (2)
Server Name | NP5650-16_6259
10.10.1.19
Model Name | NPort 5650-16
MAC Address | 00:90:E8:65:92:4A
Serial No. | 6259
Firmware Version | 3.7 Build 16082411
Serial Settings
| Alias |  | Baud rate | Data bits | Stop bits | Parity | FIFO | Flow ctrl | Interface
Port 1 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 2 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 3 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 4 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 5 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 6 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 7 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 8 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 9 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 10 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 11 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 12 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 13 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 14 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 15 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Port 16 |  |  | 115200 | 8 | 1 | None | Enable | RTS/CTS | RS-232
Operating Settings
Port | Operating mode | Packing length | Delimiter 1 | Delimiter 2 | Delimiter process | Force transmit
1 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
2 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
3 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
4 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
5 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
6 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
7 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
8 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
9 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
10 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
11 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
12 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
13 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
14 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
15 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
16 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1

## 249MOXA
Server Name | NP5650-16_6483
10.10.1.249
Model Name | NPort 5650-16
MAC Address | 00:90:E8:65:93:2A
Serial No. | 6483
Firmware Version | 3.7 Build 16082411
Serial Settings
| Alias |  | Baud rate | Data bits | Stop bits | Parity | FIFO | Flow ctrl | Interface
Port 1 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-485 2Wire
Port 2 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-485 2Wire
Port 3 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-485 2Wire
Port 4 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-485 2Wire
Port 5 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-485 2Wire
Port 6 |  |  | 9600 | 8 | 1 | None | Disable | None | RS-232
Port 7 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-485 2Wire
Port 8 |  |  | 9600 | 8 | 1 | None | Disable | None | RS-232
Port 9 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-485 2Wire
Port 10 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-485 2Wire
Port 11 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-485 2Wire
Port 12 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-485 2Wire
Port 13 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-485 2Wire
Port 14 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-485 2Wire
Port 15 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-485 2Wire
Port 16 |  |  | 9600 | 8 | 1 | None | Enable | RTS/CTS | RS-485 2Wire
Operating Settings
Port | Operating mode | Packing length | Delimiter 1 | Delimiter 2 | Delimiter process | Force transmit
1 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
2 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
3 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
4 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
5 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
6 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
7 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
8 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
9 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
10 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
11 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
12 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
13 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
14 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
15 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1
16 | Real COM Mode | 0 | 0 (Disable) | 0 (Disable) | Do Nothing | 0
|  | TCP alive check time: | 7
|  | Max connection: | 1

## 104_NPort
확정결정지은뒤에 연결작업해야겠구만
기존kepware의 설정값에 맞게 Com 하나씩 잡고 테스트가 좋을듯.
COM 정보 원본 날려버렸나염?

## TOBE_용수_구성
순번 | 구분 | 계량장비번호 | 수요가업체 | 장비모델 | Moxa ip | 포트 위치 | PC COM 포트번호 | 계량유형 | 통신종류 | Nport | DB Table | 비고 | 확인
1 | 용수 | PR_FW | 코오롱유화(PR) | NF530 | 10.10.1.17 | 4 | COM46 | 여과수(FW) | RS-232 | 9600,N,8,1 | TB_DATA_WA_PR_FW
2 | 용수 | AA_DW | 한국알콜(AA) | NF530 | 10.10.1.18 | 5 | COM63 | 순수(DW) | RS-232 | 9600,N,8,1
3 | 용수 | AA_FW | 한국알콜(AA) | NF530 | 10.10.1.17 | 12 | COM54 | 여과수(FW) | RS-232 | 9600,N,8,1
4 | 용수 | AB_DW | 이수화학(AB) | NF530 | 10.10.1.17 | 2 | COM44 | 순수(DW) | RS-232 | 9600,N,8,1
5 | 용수 | AB_FW | 이수화학(AB) | NF530 | 10.10.1.18 | 16 | COM74 | 여과수(FW) | RS-232 | 9600,N,8,1
6 | 용수 | AN_DW | 동서석유(AN) | NF530 | 10.10.1.18 | 8 | COM66 | 순수(DW) | RS-232 | 9600,N,8,1
7 | 용수 | AN_FW | 동서석유(AN) | NF530 | 10.10.1.18 | 3 | COM61 | 여과수(FW) | RS-232 | 9600,N,8,1
8 | 용수 | HX_FW | 에보닉(HX) |  |  |  |  | 여과수(FW) |  |  |  | AS-IS에 없음
9 | 용수 | MA_DW | 용산화학(MA) | NF530 | 10.10.1.17 | 9 | COM51 | 순수(DW) | RS-232 | 9600,N,8,1
10 | 용수 | MA_FW | 용산화학(MA) | NF530 | 10.10.1.17 | 3 | COM45 | 여과수(FW) | RS-232 | 9600,N,8,1
11 | 용수 | PA_DW | 애경유화(PA) | NF530 | 10.10.1.18 | 7 | COM65 | 순수(DW) | RS-232 | 9600,N,8,1
12 | 용수 | PA_FW | 애경유화(PA) | NF530 | 10.10.1.18 | 4 | COM62 | 여과수(FW) | RS-232 | 9600,N,8,1
13 | 용수 | PE_DW | 한화석유(PE) |  |  |  |  | 순수(DW) |  |  |  | AS-IS에 없음
14 | 용수 | PE_FW | 한화석유(PE) | NF530 | 10.10.1.17 | 14 | COM56 | 여과수(FW) | RS-232 | 9600,N,8,1
15 | 용수 | PP_DW | 대한유화(PP) | NF530 | 10.10.1.18 | 6 | COM64 | 순수(DW) | RS-232 | 9600,N,8,1
16 | 용수 | PP_FW | 대한유화(PP) | NF530 | 10.10.1.18 | 2 | COM60 | 여과수(FW) | RS-232 | 9600,N,8,1
17 | 용수 | PSM_DW | 금호석유(PSM) | NF530 | 10.10.1.17 | 16 | COM58 | 순수(DW) | RS-232 | 9600,N,8,1
18 | 용수 | SALT_DW | 제염공장(SALT) | NF530 | 10.10.1.17 | 13 | COM55 | 순수(DW) | RS-232 | 9600,N,8,1
19 | 용수 | SALT_FW | 제염공장(SALT) | NF530 | 10.10.1.17 | 7 | COM49 | 여과수(FW) | RS-232 | 9600,N,8,1
20 | 용수 | SKN_DW | [9 empty] | AS-IS에 없음
21 | 용수 | SKN_FW | [9 empty] | AS-IS에 없음
22 | 용수 | SM_DW | 동부하이텍(SM) | NF530 | 10.10.1.17 | 8 | COM50 | 순수(DW) | RS-232 | 9600,N,8,1
23 | 용수 | SM_FW | 동부하이텍(SM) | NF530 | 10.10.1.17 | 5 | COM47 | 여과수(FW) | RS-232 | 9600,N,8,1
24 | 용수 | TPA_FW | 삼성석유(TPA) | NF530 | 10.10.1.17 | 6 | COM48 | 여과수(FW) | RS-232 | 9600,N,8,1
25 | 용수 | TPA_FW2 | 삼성석유(TPA) | NF530 | 10.10.1.17 | 1 | COM43 | 여과수(FW) | RS-232 | 9600,N,8,1
26 | 용수 | AA_FR_FW | 한국알콜(AA) | NF530 | 10.10.1.18 | 12 | COM70 | 응축수(FR) | RS-232 | 9600,N,8,1 |  | MIT에서 조사했을때 증기로 구분됨
27 | 용수 | AA_FR_DW | 한국알콜(AA) | NF530 | 10.10.1.16 | 12 | COM38 | 응축수(FR) | RS-232 | 9600,N,8,1 |  | MIT에서 조사했을때 증기로 구분됨
28 | 용수 | PSM_FW | 금호석유(PSM) | NF530 | 10.10.1.17 | 15 | COM57 | 여과수(FW) | RS-232 | 9600,N,8,1 |  | AS-IS에만 있음
29 | 용수 | XS_DW | 케이피케미칼(XS) | NF530 | 10.10.1.17 | 11 | COM53 | 순수(DW) | RS-232 | 9600,N,8,1 |  | AS-IS에만 있음
30 | 용수 | SBR_DW | 금호석유(SBR) | NF530 | 10.10.1.18 | 1 | COM59 | 순수(DW) | RS-232 | 9600,N,8,1 |  | AS-IS에만 있음
Note on C1: 전기, 용수,스팀,전용선(???)
Note on G1: admin / moxa
Note on O1: 실제확인시 체크

## TOBE_스팀_구성
순번 | 구분 | 계량장비번호 | 수요가업체 | 장비모델 | Moxa ip | 포트 위치 | PC COM 포트번호 | 계량유형 | 통신종류 | Nport | DB Table | 비고 | 확인
1 | 증기 | AA_LP | 한국알콜(AA) | NF550 | 10.10.1.16 | 7 | COM33 | 저압(LP) | RS-232 | 9600,N,8,1
2 | 증기 | AA_MP | 한국알콜(AA) | NF550 | 10.10.1.16 | 6 | COM32 | 중압(MP) | RS-232 | 9600,N,8,1
3 | 증기 | BK_MP | 한국바스프 | M800->PLC | 10.10.1.18 |  | COM7 | 중압(MP) | RS-232 | 9600,N,8,1
4 | 증기 | BP_FR_LP | [9 empty] | as-is에 없음
5 | 증기 | BP_HP | 삼성비피(BP) | NF550 | 10.10.1.16 | 8 | COM34 | 고압(HP) | RS-232 | 9600,N,8,1
6 | 증기 | CL | [9 empty] | as-is에 없음
7 | 증기 | CL_HP | 카프로(CL) | NF550 | 10.10.1.16 | 10 | COM36 | 고압(HP) | RS-232 | 9600,N,8,1
8 | 증기 | EPS_MP | 한국바스프(EPS) | NF550 | 10.10.1.15 | 1 | COM11 | 중압(MP) | RS-232 | 9600,N,8,1
9 | 증기 | HCC2_MP | [9 empty] | as-is에 없음
10 | 증기 | HX_LP | 에보닉(HX) | NF550 | 10.10.1.15 | 13 | COM23 | 저압(LP) | RS-232 | 9600,N,8,1 |  | NF-530, Mix
11 | 증기 | KPC_FR_MP2 | 케이피케미칼(KPC) | NF550 | 10.10.1.15 | 4 | COM14 | 잉여(FR) | RS-232 | 9600,N,8,1
12 | 증기 | KPC_FR_MP4 | [9 empty] | as-is에 없음
13 | 증기 | MA_FR_HP | 용산화학(MA) | NF550 | 10.10.1.16 | 13 | COM39 | 잉여(FR) | RS-232 | 9600,N,8,1
14 | 증기 | PA_FR_LP | 애경유화(PA) | NF550 | 10.10.1.15 | 8 | COM18 | 잉여(FR) | RS-232 | 9600,N,8,1 |  | NF-530, Mix
15 | 증기 | PA_HP | 애경유화(PA) | NF550 | 10.10.1.15 | 9 | COM19 | 고압(HP) | RS-232 | 9600,N,8,1
16 | 증기 | PE_HP | [9 empty] | as-is에 없음
17 | 증기 | PP_LP | 대한유화(PP) | NF550 | 10.10.1.16 | 1 | COM27 | 저압(LP) | RS-232 | 9600,N,8,1
18 | 증기 | PP_MP | 대한유화(PP) | NF550 | 10.10.1.15 | 16 | COM26 | 중압(MP) | RS-232 | 9600,N,8,1
19 | 증기 | PP_PRI | 대한유화(PP) | NF550 | 10.10.1.15 | 15 | COM25 | 원증기(PRI) | RS-232 | 9600,N,8,1
20 | 증기 | PR_LP | 코오롱유화(PR) | NF550 | 10.10.1.15 | 6 | COM16 | 저압(LP) | RS-232 | 9600,N,8,1
21 | 증기 | PR_MP | 코오롱유화(PR) | NF550 | 10.10.1.15 | 5 | COM15 | 중압(MP) | RS-232 | 9600,N,8,1
22 | 증기 | PSM_LP | 금호석유(PSM) | NF550 | 10.10.1.15 | 11 | COM21 | 저압(LP) | RS-232 | 9600,N,8,1
23 | 증기 | PSM_LP2 | [9 empty] | as-is에 없음
24 | 증기 | PSM_MP | 금호석유(PSM) | NF550 | 10.10.1.15 | 12 | COM22 | 중압(MP) | RS-232 | 9600,N,8,1
25 | 증기 | SALT_HP | 제염공장(SALT) | NF550 | 10.10.1.15 | 2 | COM12 | 고압(HP) | RS-232 | 9600,N,8,1
26 | 증기 | SALT_LP | 제염공장(SALT) | NF550 | 10.10.1.15 | 3 | COM13 | 저압(LP) | RS-232 | 9600,N,8,1
27 | 증기 | SBR_LP1 | 금호석유(SBR) | NF550 | 10.10.1.16 | 5 | COM31 | 저압(LP) | RS-232 | 9600,N,8,1
28 | 증기 | SBR_LP2 | 금호석유(SBR) | NF550 | 10.10.1.16 | 9 | COM35 | 저압(LP) | RS-232 | 9600,N,8,1
29 | 증기 | SBR_MP | 금호석유(SBR) | NF550 | 10.10.1.16 | 4 | COM30 | 중압(MP) | RS-232 | 9600,N,8,1
30 | 증기 | SBR_MP2 | [9 empty] | as-is에 없음
31 | 증기 | SFC_HP | 삼성정밀(SFC) | NF550 | 10.10.1.18 | 9 | COM67 | 고압(HP) | RS-232 | 9600,N,8,1 |  | 한주->정밀공급
32 | 증기 | SFC_MP1 | 삼성정밀(SFC) | M800->PLC | 10.10.1.18 |  | COM2 | 중압(MP) | 모드버스 | 9600,N,8,1 |  | 모드버스(모뎀통신:공사대상제외)
33 | 증기 | SFC_MP2 | 삼성정밀(SFC) | M800->PLC | 10.10.1.18 |  | COM2 | 중압(MP) | 모드버스 | 9600,N,8,1 |  | 정밀(1), 정밀(2) Data 통신
34 | 증기 | SFCM_MP | [9 empty] | as-is에 없음
35 | 증기 | SKN_HP | [9 empty] | as-is에 없음
36 | 증기 | SKP_HP | [9 empty] | as-is에 없음
37 | 증기 | SKP_PRI | [9 empty] | as-is에 없음
38 | 증기 | SM_MP | 동부하이텍(SM) | NF550 | 10.10.1.15 | 10 | COM20 | 중압(MP) | RS-232 | 9600,N,8,1
39 | 증기 | STAC_HP | [9 empty] | as-is에 없음
40 | 증기 | TPA_FR_LP1 | 삼성석유(TPA) | NF550 | 10.10.1.16 | 15 | COM41 | 잉여(FR) | RS-234 | 9600,N,8,3 |  | NF-530, Mix, AA LP2
41 | 증기 | TPA_FR_LP2 | 삼성석유(TPA) | NF550 | 10.10.1.16 | 16 | COM42 | 잉여(FR) | RS-235 | 9600,N,8,4 |  | NF-530, Mix, 제염공장
42 | 증기 | TPA_FR_LP3 | [9 empty] | as-is에 없음
43 | 증기 | TPA_FR_MP | 삼성석유(TPA) | NF550 | 10.10.1.16 | 14 | COM40 | 잉여(FR) | RS-233 | 9600,N,8,2 |  | NF-530, Mix, AA MP2
44 | 증기 | TPA_FR_MP2 | [9 empty] | as-is에 없음
45 | 증기 | TPA_FR_MP3 | [9 empty] | as-is에 없음
46 | 증기 | TPA_FR_MP4 | [9 empty] | as-is에 없음
47 | 증기 | TPA_FR_SFC1 | 삼성석유(TPA) | NF550 | 10.10.1.18 | 10 | COM68 | 잉여(FR) | RS-232 | 9600,N,8,1 |  | 삼성->정밀1
48 | 증기 | TPA_FR_SFC2 | 삼성석유(TPA) | NF550 | 10.10.1.18 | 11 | COM69 | 잉여(FR) | RS-232 | 9600,N,8,1 |  | 삼성->정밀2
49 | 증기 | UNID_HP | [9 empty] | as-is에 없음
50 | 증기 | USA_FR_PRI | [9 empty] | as-is에 없음
51 | 증기 | CL_MP | 카프로(CL) | NF550 | 10.10.1.16 | 11 | COM37 | 중압(MP) | RS-232 | 9600,N,8,1 |  | AS-IS에만 있음
52 | 증기 | SBR_HP | 금호석유(SBR) | NF550 | 10.10.1.16 | 3 | COM29 | 고압(HP) | RS-232 | 9600,N,8,1 |  | AS-IS에만 있음
53 | 증기 | MA_HP | 용산화학(MA) | NF550 | 10.10.1.15 | 7 | COM17 | 고압(HP) | RS-232 | 9600,N,8,1 |  | AS-IS에만 있음
54 | 증기 | HX_HP | 에보닉(HX) | M200G | 10.10.1.15 | 14 | COM24 | 고압(HP) | RS-232 | 9600,N,8,1 |  | AS-IS에만 있음
55 | 증기 | PE_HP | 한화석유(PE) | NF550 | 10.10.1.16 | 2 | COM28 | 고압(HP) | RS-232 | 9600,N,8,1 |  | AS-IS에만 있음
56 | 증기 | KPC_FR_MP1 | 케이피케미칼(KPC) | M80G | 10.10.1.16 |  | COM1 | 잉여(FR) | RS-232 | 9600,N,8,1 |  | AS-IS에만 있음 모드버스(모뎀통신:공사대상제외)
57 | 증기 | KPC_FR_MP3 | 케이피케미칼(KPC) | M81G | 10.10.1.16 |  | COM3 | 잉여(FR) | RS-233 | 9600,N,8,2 |  | AS-IS에만 있음 KP->PE
Note on C1: 전기, 용수,스팀,전용선(???)
Note on G1: admin / moxa
Note on O1: 실제확인시 체크

## TOBE_전기_구성
순번 | 구분 | 계량장비번호 | 수요가업체 | 장비모델 | Moxa ip | 포트 위치 | PC COM 포트번호 | 계량유형 | 통신종류 | Nport | DB Table | 비고 | 확인
1 | 전기 | SBR1 | 금호석유(SBR) | LGRW33 | 10.10.1.11 | 1 | COM11 | 전기 | RS-232 | 9600,N,8,1
2 | 전기 | PSM2 | 금호석유(SBR) | LGRW33 | 10.10.1.11 | 2 | COM12 | 전기 | RS-232 | 9600,N,8,1
3 | 전기 | CL2 | 카프로(CL) | LGRW33 | 10.10.1.11 | 3 | COM13 | 전기 | RS-232 | 9600,N,8,1
4 | 전기 | TPA2 | 삼성석유(TPA) | LGRW33 | 10.10.1.11 | 4 | COM14 | 전기 | RS-232 | 9600,N,8,1
5 | 전기 | AB2 | 이수화학(AB) | LGRW33 | 10.10.1.11 | 5 | COM15 | 전기 | RS-232 | 9600,N,8,1
6 | 전기 | EPK5 | 대한유화(PP) | LGRW33 | 10.10.1.11 | 6 | COM16 | 전기 | RS-232 | 9600,N,8,1
7 | 전기 | PP6 | 대한유화(PP) | LGRW33 | 10.10.1.11 | 7 | COM17 | 전기 | RS-232 | 9600,N,8,1
8 | 전기 | PP7 | 대한유화(PP) | LGRW33 | 10.10.1.11 | 8 | COM18 | 전기 | RS-232 | 9600,N,8,1
9 | 전기 | HX | 에보닉(HX) | LGRW33 | 10.10.1.11 | 11 | COM19 | 전기 | RS-232 | 9600,N,8,1
10 | 전기 | PP1 | 대한유화(PP) | LGRW33 | 10.10.1.12 | 1 | COM27 | 전기 | RS-232 | 9600,N,8,1
11 | 전기 | PSM1 | 금호석유(SBR) | LGRW33 | 10.10.1.12 | 2 | COM28 | 전기 | RS-232 | 9600,N,8,1
12 | 전기 | PR | 코오롱유화(PR) | LGRW33 | 10.10.1.12 | 3 | COM29 | 전기 | RS-232 | 9600,N,8,1
13 | 전기 | PE1 | 한화석유(PE) | LGRW33 | 10.10.1.12 | 4 | COM30 | 전기 | RS-232 | 9600,N,8,1
14 | 전기 | BP2 | 삼성비피(BP) | LGRW33 | 10.10.1.12 | 5 | COM31 | 전기 | RS-232 | 9600,N,8,1
15 | 전기 | KPC1 | 케이피케미칼(PET) | LGRW33 | 10.10.1.12 | 6 | COM32 | 전기 | RS-232 | 9600,N,8,1
16 | 전기 | AEK4 | 대한유화(PP) | LGRW33 | 10.10.1.12 | 7 | COM33 | 전기 | RS-232 | 9600,N,8,1
17 | 전기 | EPS1 | 한국바스프(EPS) | LGRW33 | 10.10.1.12 | 8 | COM34 | 전기 | RS-232 | 9600,N,8,1
18 | 전기 | PE2 | 한화석유(PE) | LGRW33 | 10.10.1.12 | 9 | COM35 | 전기 | RS-232 | 9600,N,8,1
19 | 전기 | AN2 | 동서석유(AN) | LGRW33 | 10.10.1.12 | 10 | COM36 | 전기 | RS-232 | 9600,N,8,1
20 | 전기 | SPARE | F29 |  | 10.10.1.12 | 11 | COM37 | 전기 | RS-232
21 | 전기 | PA2 | 애경유화(PA) | LGRW33 | 10.10.1.13 | 1 | COM43 | 전기 | RS-232 | 9600,N,8,1
22 | 전기 | PK3 | 대한유화(PP) | LGRW33 | 10.10.1.13 | 2 | COM44 | 전기 | RS-232 | 9600,N,8,1
23 | 전기 | XS | 케이피케미칼(PET) | LGRW33 | 10.10.1.13 | 3 | COM45 | 전기 | RS-232 | 9600,N,8,1
24 | 전기 | SBR2 | 금호석유(SBR) | LGRW33 | 10.10.1.13 | 4 | COM46 | 전기 | RS-232 | 9600,N,8,1
25 | 전기 | PE4 | 한화석유(PE) | LGRW33 | 10.10.1.13 | 5 | COM47 | 전기 | RS-232 | 9600,N,8,1
26 | 전기 | EPS2 | 한국바스프(EPS) | LGRW33 | 10.10.1.13 | 6 | COM48 | 전기 | RS-232 | 9600,N,8,1
27 | 전기 | PET1 | 케이피케미칼(PET) | LGRW33 | 10.10.1.13 | 7 | COM49 | 전기 | RS-232 | 9600,N,8,1
28 | 전기 | BP1 | 삼성비피(BP) | LGRW33 | 10.10.1.13 | 8 | COM50 | 전기 | RS-232 | 9600,N,8,1
29 | 전기 | PSM3 | 금호석유(SBR) | LGRW33 | 10.10.1.13 | 9 | COM51 | 전기 | RS-232 | 9600,N,8,1
30 | 전기 | TPA3 | 삼성석유(TPA) | LGRW33 | 10.10.1.13 | 10 | COM52 | 전기 | RS-232 | 9600,N,8,1
31 | 전기 | KPC2 | 케이피케미칼(PET) | LGRW33 | 10.10.1.13 | 11 | COM53 | 전기 | RS-232 | 9600,N,8,1
32 | 전기 | SBR3 | 금호석유(SBR) | LGRW33 | 10.10.1.14 | 1 | COM59 | 전기 | RS-232 | 9600,N,8,1
33 | 전기 | CL3 | 카프로(CL) | LGRW33 | 10.10.1.14 | 2 | COM60 | 전기 | RS-232 | 9600,N,8,1
34 | 전기 | SALT | 제염공장(SALT) | LGRW33(구) | 10.10.1.14 | 3 | COM61 | 전기 | RS-232 | 2400,E,7,1
35 | 전기 | AN3 | 동서석유(AN) | LGRW33 | 10.10.1.14 | 4 | COM62 | 전기 | RS-232 | 9600,N,8,1
36 | 전기 | PET2 | 케이피케미칼(PET) | LGRW33(구) | 10.10.1.14 | 5 | COM63 | 전기 | RS-232 | 2400,E,7,1
37 | 전기 | AB1 | 이수화학(AB) | LGRW33(구) | 10.10.1.14 | 6 | COM64 | 전기 | RS-232 | 2400,E,7,1
38 | 전기 | CL1 | 카프로(CL) | LGRW33 | 10.10.1.14 | 7 | COM65 | 전기 | RS-232 | 9600,N,8,1
39 | 전기 | AN2 | 동서석유(AN) | LGRW33(구) | 10.10.1.14 | 8 | COM66 | 전기 | RS-232 | 2400,E,7,1
40 | 전기 | SM | 동부하이텍(SM) | LGRW33 | 10.10.1.14 | 9 | COM67 | 전기 | RS-232 | 9600,N,8,1
41 | 전기 | AA | 한국알콜(AA) | LGRW33 | 10.10.1.14 | 10 | COM68 | 전기 | RS-232 | 9600,N,8,1
42 | 전기 | TPA1 | 삼성석유(TPA) | LGRW33 | 10.10.1.14 | 11 | COM69 | 전기 | RS-232 | 9600,N,8,1
43 | 전기 | PE3 | 한화석유(PE) | LGRW33 | 10.10.1.14 | 12 | COM70 | 전기 | RS-232 | 9600,N,8,1
44 | 전기 | MA | 용산화학(MA) | LGRW33 | 10.10.1.14 | 13 | COM71 | 전기 | RS-232 | 9600,N,8,1
Note on C1: 전기, 용수,스팀,전용선(???)
Note on G1: admin / moxa
Note on O1: 실제확인시 체크

## ASIS_계측장비_멀티포트_구성현황
모델사양 | 세팅IP | 포트 위치 | 설정 Port번호 | PC COM 포트번호 | 계량유형 | 계량장비번호 | 수요가업체 | 장비모델 | 통신세팅 | 통신종류 | 스캔주기 | 비고
PortBase-3161 | 10.10.1.11 | 1 | 4001 | COM11 | 전기 | SBR1 | 금호석유(SBR) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
16포트 |  | 2 | 4002 | COM12 | 전기 | PSM2 | 금호석유(SBR) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 3 | 4003 | COM13 | 전기 | CL2 | 카프로(CL) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 4 | 4004 | COM14 | 전기 | TPA2 | 삼성석유(TPA) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 5 | 4005 | COM15 | 전기 | AB2 | 이수화학(AB) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 6 | 4006 | COM16 | 전기 | EPK5 | 대한유화(PP) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 7 | 4007 | COM17 | 전기 | PP6 | 대한유화(PP) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 8 | 4008 | COM18 | 전기 | PP7 | 대한유화(PP) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 16 | 4016 | COM7 | 수전 | H_TL | 한주 T/L 수전 | EMP5100 | 2400,N,8,1 | RS-485->232 | 3초 | 모드버스통신, 컨버터사용
|  | 11 | 4011 | COM19 | 전기 | HX | 에보닉(HX) | LGRW33 | 9600,N,8,1 | RS-232 | 5분 | 11. 6월 추가
| 10.10.1.12 | 1 | 4001 | COM27 | 전기 | PP1 | 대한유화(PP) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 2 | 4002 | COM28 | 전기 | PSM1 | 금호석유(SBR) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 3 | 4003 | COM29 | 전기 | PR | 코오롱유화(PR) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 4 | 4004 | COM30 | 전기 | PE1 | 한화석유(PE) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 5 | 4005 | COM31 | 전기 | BP2 | 삼성비피(BP) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 6 | 4006 | COM32 | 전기 | KPC1 | 케이피케미칼(PET) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 7 | 4007 | COM33 | 전기 | AEK4 | 대한유화(PP) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 8 | 4008 | COM34 | 전기 | EPS1 | 한국바스프(EPS) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 9 | 4009 | COM35 | 전기 | PE2 | 한화석유(PE) | LGRW33 | 9600,N,8,1 | RS-232 | 5분 | 11. 6월 추가
|  | 10 | 4010 | COM36 | 전기 | AN2 | 동서석유(AN) | LGRW33 | 9600,N,8,1 | RS-232 | 5분 | 11. 6월 추가, 3공장->1공장 이동
|  | 11 | 4011 | COM37 | 전기 | SPARE | F29 |  |  |  |  | 11. 6월 추가, 예비선로
1공장(19대)
PortBase-3161 | 10.10.1.13 | 1 | 4001 | COM43 | 전기 | PA2 | 애경유화(PA) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
16포트 |  | 2 | 4002 | COM44 | 전기 | PK3 | 대한유화(PP) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 3 | 4003 | COM45 | 전기 | XS | 케이피케미칼(PET) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 4 | 4004 | COM46 | 전기 | SBR2 | 금호석유(SBR) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 5 | 4005 | COM47 | 전기 | PE4 | 한화석유(PE) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 6 | 4006 | COM48 | 전기 | EPS2 | 한국바스프(EPS) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 7 | 4007 | COM49 | 전기 | PET1 | 케이피케미칼(PET) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 8 | 4008 | COM50 | 전기 | BP1 | 삼성비피(BP) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 9 | 4009 | COM51 | 전기 | PSM3 | 금호석유(SBR) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 10 | 4010 | COM52 | 전기 | TPA3 | 삼성석유(TPA) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 11 | 4011 | COM53 | 전기 | KPC2 | 케이피케미칼(PET) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 16 | 4016 | COM8 | 수전 | S_TL | 석지 T/L 수전 | EMP5100 | 2400,N,8,1 | RS-485->232 | 3초 | 모드버스통신, 컨버터사용
2공장(11대)
PortBase-3161 | 10.10.1.14 | 1 | 4001 | COM59 | 전기 | SBR3 | 금호석유(SBR) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
16포트 |  | 2 | 4002 | COM60 | 전기 | CL3 | 카프로(CL) | LGRW33 | 9600,N,8,1 | RS-232 | 5분 | 2010.04.26 일 신 장비변경
|  | 3 | 4003 | COM61 | 전기 | SALT | 제염공장(SALT) | LGRW33(구) | 2400,E,7,1 | RS-232 | 5분
|  | 4 | 4004 | COM62 | 전기 | AN3 | 동서석유(AN) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 5 | 4005 | COM63 | 전기 | PET2 | 케이피케미칼(PET) | LGRW33(구) | 2400,E,7,1 | RS-232 | 5분
|  | 6 | 4006 | COM64 | 전기 | AB1 | 이수화학(AB) | LGRW33(구) | 2400,E,7,1 | RS-232 | 5분
|  | 7 | 4007 | COM65 | 전기 | CL1 | 카프로(CL) | LGRW33 | 9600,N,8,1 | RS-232 | 5분 | 2010.04.26 일 신 장비변경
|  | 8 | 4008 | COM66 | 전기 | AN2 | 동서석유(AN) | LGRW33(구) | 2400,E,7,1 | RS-232 | 5분 | 11. 6월 1공장 이동
|  | 9 | 4009 | COM67 | 전기 | SM | 동부하이텍(SM) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 10 | 4010 | COM68 | 전기 | AA | 한국알콜(AA) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 11 | 4011 | COM69 | 전기 | TPA1 | 삼성석유(TPA) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 12 | 4012 | COM70 | 전기 | PE3 | 한화석유(PE) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
|  | 13 | 4013 | COM71 | 전기 | MA | 용산화학(MA) | LGRW33 | 9600,N,8,1 | RS-232 | 5분
3공장(13대)
총 대수(40 대)
PortBase-3161 | 10.10.1.15 | 1 | 4001 | COM11 | 중압(MP) | EPS_MP | 한국바스프(EPS) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 1
16포트 |  | 2 | 4002 | COM12 | 고압(HP) | SALT_HP | 제염공장(SALT) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 2
|  | 3 | 4003 | COM13 | 저압(LP) | SALT_LP | 제염공장(SALT) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 3
|  | 4 | 4004 | COM14 | 잉여(FR) | KPC_FR_MP2 | 케이피케미칼(KPC) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 4
|  | 5 | 4005 | COM15 | 중압(MP) | PR_MP | 코오롱유화(PR) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 5
|  | 6 | 4006 | COM16 | 저압(LP) | PR_LP | 코오롱유화(PR) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 6
|  | 7 | 4007 | COM17 | 고압(HP) | MA_HP | 용산화학(MA) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 7
|  | 8 | 4008 | COM18 | 잉여(FR) | PA_FR_LP | 애경유화(PA) | NF550 | 9600,N,8,1 | RS-232 | 3초 | NF-530, Mix | 8
|  | 9 | 4009 | COM19 | 고압(HP) | PA_HP | 애경유화(PA) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 9
|  | 10 | 4010 | COM20 | 중압(MP) | SM_MP | 동부하이텍(SM) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 10
|  | 11 | 4011 | COM21 | 저압(LP) | PSM_LP | 금호석유(PSM) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 11
|  | 12 | 4012 | COM22 | 중압(MP) | PSM_MP | 금호석유(PSM) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 12
|  | 13 | 4013 | COM23 | 저압(LP) | HX_LP | 에보닉(HX) | NF550 | 9600,N,8,1 | RS-232 | 3초 | NF-530, Mix | 13
|  | 14 | 4014 | COM24 | 고압(HP) | HX_HP | 에보닉(HX) | M200G | 9600,N,8,1 | RS-232 | 3초 |  | 14
|  | 15 | 4015 | COM25 | 원증기(PRI) | PP_PRI | 대한유화(PP) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 15
|  | 16 | 4016 | COM26 | 중압(MP) | PP_MP | 대한유화(PP) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 16
| 10.10.1.16 | 1 | 4001 | COM27 | 저압(LP) | PP_LP | 대한유화(PP) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 17
|  | 2 | 4002 | COM28 | 고압(HP) | PE_HP | 한화석유(PE) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 18
|  | 3 | 4003 | COM29 | 고압(HP) | SBR_HP | 금호석유(SBR) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 19
|  | 4 | 4004 | COM30 | 중압(MP) | SBR_MP | 금호석유(SBR) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 20
|  | 5 | 4005 | COM31 | 저압(LP) | SBR_LP1 | 금호석유(SBR) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 21
|  | 6 | 4006 | COM32 | 중압(MP) | AA_MP | 한국알콜(AA) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 22
|  | 7 | 4007 | COM33 | 저압(LP) | AA_LP | 한국알콜(AA) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 23
|  | 8 | 4008 | COM34 | 고압(HP) | BP_HP | 삼성비피(BP) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 24
|  | 9 | 4009 | COM35 | 저압(LP) | SBR_LP2 | 금호석유(SBR) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 25
|  | 10 | 4010 | COM36 | 고압(HP) | CL_HP | 카프로(CL) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 26
|  | 11 | 4011 | COM37 | 중압(MP) | CL_MP | 카프로(CL) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 27
|  | 12 | 4012 | COM38 | 응축수(FR) | AA_FR_DW | 한국알콜(AA) | NF530 | 9600,N,8,1 | RS-232 | 3초 | 동서잉여증기 사용하던 Port이용 | 28
|  | 13 | 4013 | COM39 | 잉여(FR) | MA_FR_HP | 용산화학(MA) | NF550 | 9600,N,8,1 | RS-232 | 3초 |  | 29
|  | 14 | 4014 | COM40 | 잉여(FR) | TPA_FR_MP | 삼성석유(TPA) | NF550 | 9600,N,8,2 | RS-233 | 4초 | NF-530, Mix, AA MP2
|  | 15 | 4015 | COM41 | 잉여(FR) | TPA_FR_LP1 | 삼성석유(TPA) | NF550 | 9600,N,8,3 | RS-234 | 5초 | NF-530, Mix, AA LP2
|  | 16 | 4016 | COM42 | 잉여(FR) | TPA_FR_LP2 | 삼성석유(TPA) | NF550 | 9600,N,8,4 | RS-235 | 6초 | NF-530, Mix, 제염공장
|  |  | PC자체 포트 | COM1 | 잉여(FR) | KPC_FR_MP1 | 케이피케미칼(KPC) | M80G | 9600,N,8,1 | RS-232 | 3초 | 모드버스(모뎀통신:공사대상제외) | 30
|  |  |  | COM3 | 잉여(FR) | KPC_FR_MP3 | 케이피케미칼(KPC) | M81G | 9600,N,8,2 | RS-233 | 4초 | KP->PE
PortBase-3161 | 10.10.1.17 | 1 | 4001 | COM43 | 여과수(FW) | TPA_FW2 | 삼성석유(TPA) | NF530 | 9600,N,8,1 | RS-232 | 3초 | 12. 10월 추가 | 1
16포트 |  | 2 | 4002 | COM44 | 순수(DW) | AB_DW | 이수화학(AB) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 2
|  | 3 | 4003 | COM45 | 여과수(FW) | MA_FW | 용산화학(MA) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 3
|  | 4 | 4004 | COM46 | 여과수(FW) | PR_FW | 코오롱유화(PR) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 4
|  | 5 | 4005 | COM47 | 여과수(FW) | SM_FW | 동부하이텍(SM) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 5
|  | 6 | 4006 | COM48 | 여과수(FW) | TPA_FW | 삼성석유(TPA) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 6
|  | 7 | 4007 | COM49 | 여과수(FW) | SALT_FW | 제염공장(SALT) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 7
|  | 8 | 4008 | COM50 | 순수(DW) | SM_DW | 동부하이텍(SM) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 8
|  | 9 | 4009 | COM51 | 순수(DW) | MA_DW | 용산화학(MA) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 9
|  | 10 | 4010 | COM52 | 순수(DW) | TPA_DW | 삼성석유(TPA) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 10
|  | 11 | 4011 | COM53 | 순수(DW) | XS_DW | 케이피케미칼(XS) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 11
|  | 12 | 4012 | COM54 | 여과수(FW) | AA_FW | 한국알콜(AA) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 12
|  | 13 | 4013 | COM55 | 순수(DW) | SALT_DW | 제염공장(SALT) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 13
|  | 14 | 4014 | COM56 | 여과수(FW) | PE_FW | 한화석유(PE) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 14
|  | 15 | 4015 | COM57 | 여과수(FW) | PSM_FW | 금호석유(PSM) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 15
|  | 16 | 4016 | COM58 | 순수(DW) | PSM_DW | 금호석유(PSM) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 16
| 10.10.1.18 | 1 | 4001 | COM59 | 순수(DW) | SBR_DW | 금호석유(SBR) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 17
|  | 2 | 4002 | COM60 | 여과수(FW) | PP_FW | 대한유화(PP) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 18
|  | 3 | 4003 | COM61 | 여과수(FW) | AN_FW | 동서석유(AN) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 19
|  | 4 | 4004 | COM62 | 여과수(FW) | PA_FW | 애경유화(PA) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 20
|  | 5 | 4005 | COM63 | 순수(DW) | AA_DW | 한국알콜(AA) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 21
|  | 6 | 4006 | COM64 | 순수(DW) | PP_DW | 대한유화(PP) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 22
|  | 7 | 4007 | COM65 | 순수(DW) | PA_DW | 애경유화(PA) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 23
|  | 8 | 4008 | COM66 | 순수(DW) | AN_DW | 동서석유(AN) | NF530 | 9600,N,8,1 | RS-232 | 3초 |  | 24
|  | 9 | 4009 | COM67 | 고압(HP) | SFC_HP | 삼성정밀(SFC) | NF550 | 9600,N,8,1 | RS-232 | 3초 | 한주->정밀공급
|  | 10 | 4010 | COM68 | 잉여(FR) | TPA_FR_SFC1 | 삼성석유(TPA) | NF550 | 9600,N,8,1 | RS-232 | 3초 | 삼성->정밀1
|  | 11 | 4011 | COM69 | 잉여(FR) | TPA_FR_SFC2 | 삼성석유(TPA) | NF550 | 9600,N,8,1 | RS-232 | 3초 | 삼성->정밀2
|  |  | PC 자체 포트 | COM2 | 중압(MP) | SFC_MP1 SFC_MP2 | 삼성정밀(SFC) | M800->PLC | 9600,N,8,1 | 모드버스 | 3초 | 모드버스(모뎀통신:공사대상제외)
정밀(1), 정밀(2) Data 통신
|  |  |  | COM7 | 중압(MP) | BK_MP | 한국바스프 |  | 9600,N,8,1 | RS-232 | 3초
|  | 12 | 4012 | COM70 | 응축수(FR) | AA_FR_FW | 한국알콜(AA) | NF530 | 9600,N,8,1 | RS-232 | 3초
|  | 16 | 4016 | COM74 | AB_FW | 이수화학(AB) | NF530 | NF530 | 9600,N,8,1 | RS-232 | 3초